## Sheet1
Calculation for Motor 1 A/B
Rating (HP) at 480V | 75
Ampacity | 96 | NEC 430.250
Conductor Multiplier (125% of FLA) | 1.25
Calculated Conductor Current | 120
Derating for Cable Tray ( >41 conductors) | 0.35 | NEC 310.15(B)(3)(a)
Conductor Rating | 1AWG | NEC 310.15(B)(16)
Select Conductor Number and Size (Table 2) | 1-3Conductor-1AWG |  | ``
Part Number | 1STRXHHW | Ref 1
Conduit Size | 1-1/4"
1300% of FLA | 1248
Code Letter | J
Max LRA Multiplier for Code 'J' | 7.99 | NEC 430.7(B)
Max LRA for Code 'J' | 767.04
215% of Max LRA | 1649.136
Min LRA Multiplier for Code 'J' | 7.1
Min LRA for Code 'J' | 681.6
215% of Min LRA | 1465.44
Maximum Ampacity for MCP (Protect Process) | 1649.136
MCP Specifications | HMCP250L5C | Ref 2
Cam setting for MCP | D (J frame)
SF (Assumed SF = 1.0) | NA
O/L Current Multiplier | 1.15
O/L Setting | 110.4
Starter size | Size 4 | Ref 3
MCC Space required (Multiple of 6") | 4
Transformer for control circuit (VA) | 250 | Ref 4
Current in Primary of the Control Transformer (Amp) | 0.52083
125% of the Primary Current | 0.65104 | NEC 210.20(A)
Choose a Fuse with Disconnect (Go to next) (Amp) | 0.7
Choose 2 Fuse with Rating (Amp) | 0.7 | Ref 4
Current in Secondary of the Control Transformer (Amp) | 2.0833
125% of the Primary Current | 2.6042
Choose a Fuse (Go to next) (Amp) | 2.75
Choose 1 Fuse with Rating (Amp) | 2.75
Control Circuit Cable (HOA, 2 LED & Flow Switch) | 12AWG
Part Number | 12STRXHHW | Ref 1
HOA (For Field Switch) | EFSC2561 | Ref 5
Calculation for Motor 2 A/B
Rating (HP) at 480V | 100
Ampacity | 124 | NEC 430.250
Conductor Multiplier (125% of FLA) | 1.25
Calculated Conductor Current | 155
Derating for Cable Tray ( >41 conductors) | 0.35 | NEC 310.15(B)(3)(a)
Conductor Rating | 2/0 AWG | NEC 310.15(B)(16)
Select Conductor Number and Size (Table 2) | 1-3Conductor-2/0 AWG
Part Number | 2/0STRXHHW | Ref 1
Conduit Size | 1-1/2"
1300% of FLA | 1612
Code Letter | K
Max LRA Multiplier for Code 'J' | 8.99 | NEC 430.7(B)
Max LRA for Code 'J' | 1114.76
215% of Max LRA | 2396.734
Min LRA Multiplier for Code 'J' | 8
Min LRA for Code 'J' | 992
215% of Min LRA | 2132.8
Maximum Ampacity for MCP (Protect Process) | 2396.734
MCP Specifications | HMCP400N5C | Ref 2
Cam setting for MCP | E (K frame)
SF | 1.2
O/L Current Multiplier | 1.25
O/L Setting | 155
Starter size | Size 4 | Ref 3
MCC Space required (Multiple of 6") | 4
Transformer for control circuit (VA) | 250 | Ref 4
Current in Primary of the Control Transformer (Amp) | 0.52083
125% of the Primary Current | 0.65104 | NEC 210.20(A)
Choose a Fuse with Disconnect (Go to next) (Amp) | 0.7
Choose 2 Fuse with Rating (Amp) | 0.7
Current in Secondary of the Control Transformer (Amp) | 2.0833
125% of the Primary Current | 2.6042
Choose a Fuse (Go to next) (Amp) | 2.75
Choose 1 Fuse with Rating (Amp) | 2.75
Control Circuit Cable (HOA, 2 LED) | 12AWG
Part Number | 12STRXHHW | Ref 1
HOA (Class B Hydrogen) | EFSC3561 | Ref 5
Calculation for Motor 3 A/B
Rating (HP) at 480V | 125
Ampacity | 156 | NEC 430.250
Conductor Multiplier (125% of FLA) | 1.25
Calculated Conductor Current | 195
Derating for Cable Tray ( >41 conductors) | 0.35 | NEC 310.15(B)(3)(a)
Conductor Rating | 3/0 AWG | NEC 310.15(B)(16)
Select Conductor Number and Size (Table 2) | 1-3Conductor-3/0 AWG
Part Number | 3/0STRXHHW | Ref 1
Conduit Size | 1-1/2"
1300% of FLA | 2028
Code Letter | J
Max LRA Multiplier for Code 'J' | 7.99 | NEC 430.7(B)
Max LRA for Code 'J' | 1246.44
215% of Max LRA | 2679.846
Min LRA Multiplier for Code 'J' | 7.1
Min LRA for Code 'J' | 1107.6
215% of Min LRA | 2381.34
Maximum Ampacity for MCP (Protect Process) | 2679.846
MCP Specifications | HMCP400R5C | Ref 2
Cam setting for MCP | E (K frame)
SF | 1.2
O/L Current Multiplier | 1.25
O/L Setting | 195
Starter size | Size 5 | Ref 3
MCC Space required (Multiple of 6") | 6
Transformer for control circuit (VA) | 400 | Ref 4
Current in Primary of the Control Transformer (Amp) | 0.83333
125% of the Primary Current | 1.0417 | NEC 210.20(A)
Choose a Fuse with Disconnect (Go to next) (Amp) | 1.25
Choose 2 Fuse with Rating (Amp) | 1.25
Current in Secondary of the Control Transformer (Amp) | 3.3333
125% of the Primary Current | 4.1667
Choose a Fuse (Go to next) (Amp) | 4.25
Choose 1 Fuse with Rating (Amp) | 4.25
Control Circuit Cable (HOA, 2 LED) | 12AWG
Order Code | 12STRXHHW | Ref 1
HOA | EFSC2561 | Ref 5
Capacitor for Motor 3 A/B
Full Load Efficiency (From Table) | 0.91
Power Factor | 0.82
Power input (kW) | 102.4725
S Input (kVA) | 124.9665
Q (kVAR) | 71.5263
Improved Power Factor To | 0.94
Improved S (Power Input kVA) | 109.0133
Improved Q (Power Input kVAR) | 37.1926
Correction for kVAR | 34.3337
Choose Standard Capacitor Bank | 35 | Ref 6
New kVAR with Improvement | 36.5263
New S (Power Input) | 108.7878
New Power Factor (After Improvement) | 0.94195
I_cap (Amp) | 42.0985
Conductor Rating (135%) | 56.8329
One third of Motor Conductor is | 66.6667
Conductor Rating | 4 AWG | Ref 1
Select Conductor Number and Size (Table 2) | 1-3Conductor-4 AWG
Part Number | 4STRXHHW
Protection (Fuses of I_cap 250%) | 105.2461
Choose 3 Fuses with Disconnect Switch | 3-100A Fuses
Calculation for Motor 4 A/B
Rating (HP) at 480V | 150
Ampacity | 180 | NEC 430.250
Conductor Multiplier (125% of FLA) | 1.25
Calculated Conductor Current | 225
Derating for Cable Tray ( >43 conductors) | 0.35 | NEC 310.15(B)(3)(a)
Conductor Rating | 4/0 AWG | NEC 310.15(B)(16)
Select Conductor Number and Size (Table 2) | 1-3Conductor-4/0 AWG
Part Number | 4/0STRXHHW | Ref 1
Conduit Size | 2"
1300% of FLA | 2340
Code Letter | H
Max LRA Multiplier for Code 'J' | 7.09 | NEC 430.7(B)
Max LRA for Code 'J' | 1276.2
215% of Max LRA | 2743.83
Min LRA Multiplier for Code 'J' | 6.3
Min LRA for Code 'J' | 1134
215% of Min LRA | 2438.1
Maximum Ampacity for MCP (Protect Process) | 2743.83
MCP Specifications | HMCP400R5C | Ref 2
Cam setting for MCP | E (K frame)
SF | 1.18
O/L Current Multiplier | 1.25
O/L Setting | 225
Choose Variable Frequency Drive Starter | 480V SVX9000 Drives | Ref 7
Bypass Starter size | Size 5 | Ref 3
MCC Space required (Multiple of 6") | 12
Transformer for control circuit (VA) | 400 | Ref 4
Current in Primary of the Control Transformer (Amp) | 0.83333
125% of the Primary Current | 1.0417 | NEC 210.20(A)
Choose a Fuse with Disconnect (Go to next) (Amp) | 1.25
Choose 2 Fuse with Rating (Amp) | 1.25
Current in Secondary of the Control Transformer (Amp) | 3.3333
125% of the Primary Current | 4.1667
Choose a Fuse (Go to next) (Amp) | 4.25
Choose 1 Fuse with Rating (Amp) | 4.25
Control Circuit Cable (HOA, 2 LED) | 12AWG
Part Number | 12STRXHHW | Ref 1
HOA | EFSC2561 | Ref 5
Transformer
Voltage Primary | 480
Voltage Secondary | 208
Rating kVA | 45
Primary Current | 90.211
125% of Primary Conductor Ampacity | 112.7637
Choose Conductor from Table 2 | 2AWG
Order Quantity | 1-3C - 2AWG
MCCB (300% of Primary Current) | 270.6329
Choose MCCB | 250A | Ref 8
Order Code | KDC3250
MCC Space required (Multiple of 6") | 6X
Transformer Panel Board
Voltage | 208/120
Rating used for calculation (kVA) (Client Requested) | 75
Current | 208.1792
125% of Current | 260.224
Conductor Rating (Table 2) | 300kcmil | NEC 310.15(B)(16)
Choose 4C conductors from Table 2 (295A) | 1-4Conductor-300kcmil
125% of Secondary Current (Fuse Calculation) (Amp) | 260.224
Choose MCCB | 250A | Ref 8
Order Code | KDC3250
Panel Board | PRL3a | Ref 9
Welding Panel Board
Voltage | 480
Rating (Amp) | 400
Conductor size | 600 kcmil | NEC 310.15(B)(16)
Choose 3 conductors / phase | 1-3C - 600 kcmil
MCCB (250% of Rated Current) Check for Panel Board | 1000 | Ref 1
Choose MCCB | 800A | Ref 8
Order Code | MDLB3800
MCC Space required (Multiple of 6") | 6X
Feeder
Voltage | 480
Biggest Motor Load | 156
MCCB Current for Biggest Motor Load (250%) | 390
Choose MCCB for biggest motor | 390
MCCB with rating not Exceeding Calculated Value | 450
Total Current for MCCB | 1848.211
MCCB rating not Exceeding Calculated Value (AMP) | 1600
For future Expansion choose 2000A FRAME | 2000
125% of the Frame Rating (Amp) | 2500
Parallel Run needed | 6.3291
Conductor Needed | 7
Current in each conductor/phase (Amp) | 357.1429
Conductor size | 500 kcmil (395A)
Choose 3conductors / phase | 7-3Conductor-500 kcmil
MCC
Frame Size (Amp) | 2000
Choose Bus Bar (Amp) | 65000
Space Required in MCC Multiple of 6"
M1-A | 4
M1-B | 4
M2-A | 4
M2-B | 4
M3-A | 6
M3-B | 6
M4-A | 400
M4-A Bypass | 6
M4-B | 400
M4-B Bypass | 6
Transformer | 6
Welding Panel Board | 6
Future growth (Customer Requested) | 12
Total | 864
Multiple of unit (12 X 6" in a unit) | 72
Order 20" wide 2000A frame (number of units) | 72